Category 6e - User Beware

There are cables marked as Category 6e on the market. These are NOT the same as Category 6A.   Category 6e cables may perform well beyond the requirements of category 6, but do not meet the strict alien crosstalk requirements of ANSI/ TIA/EIA-568-B.2-10 Category 6A. 
  
If you require 10GBASE-T support for the full distance of a 100 m (328 ft) channel, ensure you specify that the cable meets the requires of the draft standard, ANSI/ TIA/EIA-568-B.2-10 Augmented Category 6, as a minimum.