Consolidation Point (CP)

A common question asked about CPs, is whether there is a minimum distance the should be from the Floor Distributor (FD)? Yes, but be careful. It depends on which standard you are referring to! There is a MAJOR difference in the standards, which is causing confusion. Consultants see should so ignore it and design links where the CP is less than 15 meters! Please don't, our experience shows that you should avoid links where the CP is less than 15 meters.

ISO/IEC11801:2002 
5.7.6 Consolidation point 
IV. for balanced cabling, the consolidation point shall be located so that there is at least 15 m from it to the floor distributor. 


ANSI/TIA/EIA 568-B.1 (April 12, 2001) 
6.4.2 Consolidation point 
For copper cabling, in order to reduce the effect of multiple connections in close proximity on NEXT loss and return loss, the consolidation point should be located at least 15 m (49 ft) from the telecommunications room. 

The consolidation point can be either a 110 Style IDC connection or an RJ45 / Jack connection.