DUALmode Testing

What is this? 
This is a feature related to a competitive tester the – LANTEK 6/7. 
  
What does it do? 
It reports channel and permanent link test results simultaneously. Adds only an additional 2 seconds to the Autotest time. (Category 6 = 23 seconds) 
  
Why doesnt the DTX, DSP or OMNIScanner do this? 
The method Ideal Industries prescribes is technically incorrect. 
  
A channel test involves testing the entire link with the user cords. If those user cords are replaced by another set of cords, the previous channel measurement is no longer valid and the test will have to be repeated. For this reason, the standards bodies created the permanent link test, which excludes the user cords. 
  
Let's look at the process of DUALmode testing for the LANTEK 6/7:

- Calibrate patch cords to tester

- Connect the LANTEK to the link you wish to test

- Run the Autotest

- Save the results

- Move on to the next link under test

You are not leaving the test leads behind, as required for channel testing. 
This is clearly stated in the cabling standards ANSI/TIA/EIA-568-B, ISO/IEC 11801:2002 and EN50173:2002.

Therefore, the Channel test result being reported is meaningless.

DUALmode testing can work but... ... 
To implement DUALmode testing correctly, you would have to:

- Calibrate patch cords to tester

- Connect the LANTEK to the link you wish to test

- Run the Autotest

- Save the results

- Remove the patch cords from tester and leave them connected to the link

- Move on to the next link under test

- Calibrate next set of patch cords (Takes approx. 75 seconds)

- Connect the LANTEK to the link you wish to test

- Run the Autotest

- Save the ... ... ... ... ..

You would have to calibrate a new set of patch cords for each link you test. This calibration process takes approximately 75 seconds.